| REPORT OF ELECTRIC ENERGY REDUCER TESTS |
| --- |
| TESTED DEVICE DATA |
| MODEL: | 35kVA / 50 A |
| YEAR OF PRODUCTION: | 2012 |
| MANUFACTURER: | MONODIA, Skariny 15, Mińsk, Białoruś |
| SUPPLIER: | ELRED, Urbanistów 8/40, 02-397 Warszawa |
| MEASURING DEVICE DATA |
| MODEL: | 435 |
| MANUFACTURER: | FLUKE |
| POWER RECEIVERS DATA |
| POWER DISTRIBUTION CABINET : | R07 (lighting) |
| RECEIVERS: | 170 T8 fluorescent lamps 18W + 381 fluorescent lamps T8 36W |
| NOMINAL POWER: | 16,776 kW |
| COMPARISON OF 24 HOUR ENERGY CONSUMPTION |
| 24 HOUR ENERGY CONSUMPTION without reducer with reducer savings (%) ACTIVE (kWh) 473,27 405,51 14,32 REACTIVE (kVARh) 376,04 262,44 30,21 ratio reactive/active (%) 79,46 64,72 |
| COMPARISON OF AVERAGE PHASE CURRENT |
| AVG. PHASE CURRENT without reducer with reducer L1 (A) 28,80 26,37 L2 (A) 47,11 37,67 L3 (A) 27,17 22,53 |
| CONCLUSIONS |
| Measurments have showed that installation of the reducer give following results: Significant drop of active energy consumption (aprox. 15%), Even bigger drop reactive energy consumption (aprox. 30%), Drop of reactive/active energy ratio (from aprox. 80 to 65%), despite the presence of the reactive power compensation system, Equalization of phase currents (reduction of phase current spread from 20 to 15A). |
| INSTALLATION AND MESURMENTS SUPERVISION |
| Grzegorz Rygielski Maintenance Manager |